# Text boxes

Enclosures

Low Voltage (600 volts or less)
Enclosure shall be of heavy gauge Galvanneal cold rolled steel with baked enamel finish. All mounting hardware shall be stainless steel.

Indoor enclosure shall have a screened cover with maximum openings of 1/2".

Outdoor enclosure shall have a solid heavy gauge top cover, slightly overhung to prevent ingress of rain or sleet.

CSA Approved Low Voltage
Separate external terminal junction boxes shall be provided for termination of the neutral conductor and the ground conductor. All of the other requirements outlined above shall be met.

Medium Voltage (above 600 volts to 5,000 volts)
The frame of the enclosure shall be made from structural steel angles made from heavy gauge steel, welded together, or bolted together with stainless-steel hardware. The top of the enclosure shall be solid, slightly overhung and sloped. It shall be embossed with stiffening ribs. The enclosure shall have forged eyebolts in each corner for lifting purposes.

The bottom of the enclosure shall be screened with expanded or perforated metal with openings of 1/2" or less. This screening shall be welded or bolted in and is not removable. It shall be elevated 4 to 6 inches above the base of the unit.

Bolt-on side covers on all four sides shall be used. Screened covers may be furnished for certain applications. Stainless-steel hardware shall be used. Louvered or screened openings shall not exceed 1/2".

A durable nameplate, permanently attached to one side cover shall show the manufacturer and the complete rating.

Painted enclosures shall be suitably sanded, cleaned, primed and painted. Stainless-steel and aluminum enclosures (in particular) shall be protected from scratching during manufacture, assembly and shipment.

Specification for Low or Medium Voltage, High Resistance Type Grounding Resistors

Scope

This specification covers design, manufacture and testing of low- or medium-voltage, high-resistance type Neutral Grounding Resistors (NGR) for installation indoors and outdoors onto a concrete pad or power transformer.

Applicable Standards

The NGR shall be designed, manufactured and tested as per the latest revisions of IEEE-32.

Resistors

The resistive elements shall be low temperature coefficient, resistor grade stainless steel or nickel chromium rigidly supported at each end to allow for expansion due to heating.

The resistors shall be mounted in corrosion resistant support frames, using stainless-steel hardware.

For low voltage, continuous rated above 10 amp, and all medium voltage applications, the entire resistor frame shall be mounted on insulators rated for the system voltage.

All resistor terminals and interconnections between units shall be stainless-steel, using stainless-steel hardware including lock washers. High current connections shall be spot or TIG welded as appropriate.

Connections between resistors and bushings or current transformers shall be solid copper or stainless steel bus or copper cables.